Deiiang ¦ Cleanroom World Modular Cleanroom Solutions

MODULAR CLEANROOMS

Hardwall  ·  Softwall  ·  Clean Booth

Development  |  Production  |  Sales  |  After-sales Service

Deiiang Cleanroom Technology Co., Ltd.

B102, Building 6, Erqi Industrial Park, Jiang'an District,

Wuhan City, Hubei Province, China

Tel: +86 027 82289886   |   Mobile: +86 136 3863 2902

Email: Jason@cleanroomequips.com   |   Web: www.cleanroomequips.com

CONTENTS

CATALOG INDEX

01  Hardwall Cleanroom
Rigid aluminum frame + panel / glass enclosure

02  Softwall Cleanroom
Aluminum frame + anti-static PVC curtain

03  Clean Booth
Localized workstation enclosure on aluminum profile

04  FFU & HEPA Platform
AC/DC fan filter units, H14/U15 filtration

05  Certifications
CE, RoHS, EN 1822, ISO 14644

06  Packing & Export
Knocked-down packing, container loading

HARDWALL CLEANROOM

RIGID MODULAR ENCLOSURE FOR LONG-TERM CLASSIFIED PRODUCTION

Product Description / 产品说明

■  Constructed on anodized extruded aluminum frame with sealed sandwich panel, HPL, acrylic or tempered-glass infill.

■  Suitable for ISO 5–8 per ISO 14644-1; positive or negative pressure cascade available.

■  Flush double-glazed observation windows, steel cleanroom doors with drop-down bottom seal.

■  Panels: rock-wool / glass-magnesium / paper-honeycomb / aluminum-honeycomb / PU core options.

■  HEPA H14 (EN 1822) as standard; ULPA U15/U16 option. ESD-safe conductive finish for electronics.

Product Parameters / 产品参数

| Parameter / 项目 | Specification / 规格 |
| --- | --- |
| ISO class | ISO 5 / 6 / 7 / 8 per ISO 14644-1 |
| Airflow | Unidirectional at critical zones; turbulent for support areas |
| Pressure | Positive cascade 10–15 Pa; negative-pressure containment option |
| Filtration | G4 + F8 pre-filter + H14 HEPA; U15/U16 ULPA optional |
| Temperature / RH | 18–24 °C, 30–60 % RH (custom) |
| Frame | Anodized aluminum extrusion |
| Wall panels | 50 mm hand-made sandwich panel, steel skin, rock-wool / MgO / honeycomb core |
| Door | Steel cleanroom door, tempered-glass vision panel, auto drop-seal |

SOFTWALL CLEANROOM

FLEXIBLE PVC-CURTAIN ENCLOSURE, FAST DEPLOYMENT

Product Description / 产品说明

■  Same aluminum frame and FFU platform as hardwall; perimeter enclosed with anti-static PVC curtains.

■  ISO 5–8 per ISO 14644-1; H14 HEPA standard; demountable and relocatable.

■  Surface resistance 10^6–10^9 Ω; cleanroom-grade, wipe-down compatible.

■  Typical installation 1–2 days on site; no wet trade; ideal for spot-cleaning around a machine.

■  Optional caster wheels for portable / temporary clean zones.

Product Parameters / 产品参数

| Parameter / 项目 | Specification / 规格 |
| --- | --- |
| ISO class | ISO 5 – ISO 8 |
| Wall | Anti-static PVC curtain, transparent strip, surface resistance 10^6–10^9 Ω |
| Frame | Anodized aluminum profile, bolted, demountable |
| FFU | AC or energy-saving DC FFU; 575×575 / 1175×575 / 1175×1175 mm |
| Filtration | H14 HEPA standard; U15/U16 ULPA option |
| Pressure | Positive relative to workshop; negative option for local containment |
| Temperature / RH | 18–24 °C / 30–60 % RH with conditioned make-up air |
| Installation | 1–2 days standard; fully relocatable |

CLEAN BOOTH

LOCALIZED WORKSTATION ENCLOSURE ON INDUSTRIAL ALUMINUM PROFILE

Product Description / 产品说明

■  Built on industrial aluminum extrusion (40×40 / 40×80 / 80×80 / 50×50 / 60×60 mm).

■  Infill options: clear acrylic, tempered glass, anti-static PVC curtain, or steel panel.

■  Topped by one or more FFUs with H14 HEPA / U15 ULPA; achieves ISO 5–7 at the work zone.

■  Positive or negative configuration per GMP/FDA / Risk-MaPP requirement.

■  Optional caster wheels; relocatable between production lines.

Product Parameters / 产品参数

| Parameter / 项目 | Specification / 规格 |
| --- | --- |
| Frame sections | 40×40, 40×80, 80×80, 50×50, 60×60 mm |
| Profile wall thickness | 1.5 / 2.0 / 2.5 / 3.0 mm |
| Infilling | Acrylic / tempered glass / anti-static PVC / steel panel |
| FFU | AC or EC/DC; 575×575 / 1175×575 / 1175×1175 mm; H14 / U15 |
| Achievable class | ISO 1–8 by design; typically ISO 5–7 at workstation |
| Pressure | Positive or negative |
| Mobility | Optional lockable casters |
| Lighting | Integrated LED, sealed, local switched |

FFU & FILTRATION PLATFORM

SHARED AIR-HANDLING PLATFORM ACROSS ALL THREE PRODUCT LINES

Fan Filter Unit / 风机过滤单元

■  AC single/multi-speed FFU, or energy-saving DC (EC) fan FFU with PWM speed control.

■  Standard sizes: 575×575 mm, 1175×575 mm, 1175×1175 mm.

■  HEPA H14 per EN 1822: minimum efficiency 99.995% on MPPS; ULPA U15/U16 optional.

■  Pre-filtration: G4 intake + F8 medium filter to extend HEPA life.

■  Local speed control; optional group controller with RS-485 / Modbus, filter-dP alarm, BMS/EMS interface.

■  Typical noise < 60 dB(A) at 1 m; vibration-isolating mounting standard.

Reference ACH Ranges / 参考换气次数

| ISO Class | Reference ACH range |
| --- | --- |
| ISO 3 | 360 – 540 |
| ISO 4 | 300 – 540 |
| ISO 5 | 240 – 480 |
| ISO 6 | 50 – 60 |
| ISO 7 | 30 – 40 |
| ISO 8 | 15 – 25 |

CERTIFICATIONS

DOCUMENTS SUPPLIED WITH EXPORT ORDERS

Available Certifications / 可提供证书

■  CE Declaration of Conformity for FFU / electrical control panel (EMC + LVD directives).

■  RoHS test report for FFU and control components (TÜV SÜD tested).

■  HEPA/ULPA filter test certificates per EN 1822-1 / -2 / -4 (per-filter scan).

■  ISO 16890:2022 classification report for outdoor-air intake pre-filters.

■  ISO 14644-1 at-rest classification test report (after installation, by Deiiang or third party).

■  Material certificates: panel coating, aluminum alloy, EPDM/silicone gasket, anti-static PVC.

■  Fire-rating declaration for rock-wool / MgO core panels.

Example: TÜV SÜD CE / RoHS compliance certificate for Deiiang FFU control panels

PACKING & EXPORT

KNOCKED-DOWN, CONTAINER-OPTIMISED EXPORT PACKING

Packing Details / 包装明细

■  Aluminum profiles: PE film wrap, strapped on plywood pallets, labelled by part number.

■  Sandwich panels: edge-protected, flat-packed in plywood crates, EPE-foam separated.

■  FFUs: double-wall carton with foam corners; HEPA element sealed in plastic; one unit per carton.

■  Doors & windows: edge-protected, carton + plywood frame, glass side marked 'FRAGILE — THIS SIDE UP'.

■  Electrical panels: sealed carton with desiccant, palettised.

■  Hardware kit: one labelled accessory box per room (fasteners, gaskets, hinges, cables).

■  Documentation pouch on lead package: packing list, commercial invoice, CE DoC, filter certificates, as-built drawings, installation manual, test-report templates.

Container Loading / 集装箱装载

■  Typical 40'HQ carries approx. 80–120 m² hardwall panel face area + associated FFUs and doors.

■  Incoterms: EXW / FOB Shenzhen standard; CIF Hamburg / Bremerhaven available on request.

Information Required for Firm Quotation / 询价所需资料

■  Product and process: sterile vs non-sterile; any potent / cytotoxic dust.

■  Room schedule: name, dimensions (L×W×H), required ISO class per room.

■  Site conditions: supply voltage (400 V 3Ph 50 Hz), floor load, ceiling height, door size.

■  Documentation expectations: third-party certificates and on-site qualification support.

■  Target delivery date and preferred Incoterm.

Deiiang Cleanroom Technology Co., Ltd.

B102, Building 6, Erqi Industrial Park, Jiang'an District, Wuhan, Hubei, China

Tel: +86 027 82289886   Mobile: +86 136 3863 2902

Email: Jason@cleanroomequips.com   Web: www.cleanroomequips.com